## Disclaimer
---------DISCLAIMER--------- AS NOTED IN THE LICENSE, ALLIANCE FOR ENERGY INNOVATION, LLC: (i) DISCLAIMS ANY WARRANTIES, EXPRESS OR IMPLIED, INCLUDING BUT NOT LIMITED TO ANY IMPLIED WARRANTIES OF MERCHANTABILITY, FITNESS FOR A PARTICULAR PURPOSE, TITLE OR NON-INFRINGEMENT, AND (ii) DOES NOT ASSUME ANY LEGAL LIABILITY OR RESPONSIBILITY FOR THE ACCURACY, COMPLETENESS, OR USEFULNESS OF SOFTWARE OR ITS OUTPUTS. ANY RELIANCE BY THE USER ON THE SOFTWARE IS DONE AT THE USER’S OWN RISK. BlendPATH was developed to provide the user with economic analytical capabilities to evaluate potential natural gas transmission pipeline modifications for accommodating hydrogen blending or pure hydrogen streams and to assess the potential associated economic impacts. This model is intended for use during the early stages of pipeline repurposing concept evaluation, which is defined here as the initial project phase when the developer has already gathered the relevant pipeline material design and operation data but has not yet conducted the detailed pipeline materials testing, as specified in ASME B31.12, or performed the in-line inspections that qualify a given pipeline section for hydrogen or hydrogen blending service. Despite BlendPATH using ASME B31.12 to assess existing natural gas transmission pipelines and establish potential pipeline modifications for a natural gas transmission pipeline network to meet ASME B31.12 design requirements, BlendPATH does not qualify the examined pipeline network or modifications thereof for pure hydrogen or hydrogen blending. Pipeline owners and operators must conduct additional evaluations as specified in ASME B31.12 and other relevant code and regulations, independent of BlendPATH application, to qualify actual natural gas transmission pipelines for operation with hydrogen. Failure to do so may result in pipeline fatigue and/or rupture. It is the sole responsibility of the pipeline owner and operator to ensure that their pipeline qualifies for the ASME B31.12 design option that they choose, and any other relevant code and regulations, and that any defects present in the pipeline are acceptable at the operating pressure chosen. ----------------------------

## Inputs
Name | Value
Network name | examples/wangetal2018
Save directory | out
Design option - original | a
Location class | 1
Joint factor | 1
T de-rating factor | 1
Compression ratio | [1.2, 1.4, 1.6, 1.8, 2.0]
Blending ratio | 0.5
Natural gas cost ($/MMBTU) | 7.39
H2 cost ($/kg) | 4.4076
Electricity cost ($/kWh) | 0.07
Final outlet pressure (MPa-g) | 3.325
Region | GP
Modification method | ac
Modification design option | b
Equation of state | rk
Inline inspection inspection interval | 3
Original pipeline depreciated cost | 0
Are added compressors electric? | FALSE
Are existing compressors converted to electric? | FALSE
New gas compressor isentropic efficiency | 0.78
New electric compressor isentropic efficiency | 0.88
New gas compressor driver efficiency | 0.357
New electric compressor driver efficiency
Pipe price markup | 1
Compressor price markup | 1
Financial overrides | {}
Filename suffix
Thermodynamic curvefits enabled | TRUE
Composition tracking enabled | FALSE
Scenario type | transmission
Polymer cost type | socal
Max velocity allowed in distribution networks | 20

## Results
Parameter | Value | Units
LCOT: Levelized cost of transport | 0.74795 | $/MMBTU
LCOT: New pipe CapEx | 0 | $/MMBTU
LCOT: New compression capacity CapEx | 0.13256 | $/MMBTU
LCOT: Refurbished compressor capacity CapEx | 0.032498 | $/MMBTU
LCOT: Supply compressor CapEx | 0 | $/MMBTU
LCOT: Meter & regulator station modification CapEx | 0.0067155 | $/MMBTU
LCOT: Valve replacement CapEx | 0.015921 | $/MMBTU
LCOT: Original network residual value | 0 | $/MMBTU
LCOT: In-line inspection | 0.017018 | $/MMBTU
LCOT: Compressor fuel | 0.47955 | $/MMBTU
LCOT: Compressor fuel (electric) | 0 | $/MMBTU
LCOT: Supply commpressor fuel (electric) | 0 | $/MMBTU
LCOT: Supply commpressor fuel | 0 | $/MMBTU
LCOT: Meter set assembly | 0 | $/MMBTU
LCOT: Gas pressure regulation and metering station | 0 | $/MMBTU
LCOT: Fixed O&M | 0.0081054 | $/MMBTU
LCOT: Taxes | 0.052108 | $/MMBTU
LCOT: Financial | 0.0034742 | $/MMBTU
Hydrogen injection price | 4.4076 | $/kg
Natural gas price | 7.39 | $/MMBTU
Blended gas price | 13.5472 | $/MMBTU
Pipeline capacity (daily) | 527617.1847 | MMBTU/day
Pipeline capacity (hour) | 21984.0494 | MMBTU/hr
Added pipeline | 0 | km
Added pipeline | 0 | mi
Added compressor stations | 16
Added compressor capacity | 91604.7857 | hp
Compressor fuel usage | 18676.7237 | MMBTU/day
Compressor fuel usage | 778.1968 | MMBTU/hr
Compressor fuel usage (electric) | 0 | kW
New pipe | 0 | $
New compressor stations | 206997933.8721 | $
Compressor station refurbishment | 50748077.0702 | $
Meter station modification | 10486757.2947 | $
Valve modifications | 24862120 | $
Meter set assembly | 0 | $
Gas pressure regulating metering station | 0 | $
Hydrogen energy ratio | 24.2409 | %
Emissions intensity (total) | 49.9149 | kgCO2e/MMBTU
Total emissions (annual) | 9.6126 | MMTCO2e/yr
Breakdown of original pipe by diameter, schedule and grade
Pipe Nominal Diameter | Length (km) | Grade | Schedule | Polymer
650 | 400 | X60 | S Std
Breakdown of new pipe by diameter, schedule and grade
Pipe Nominal Diameter | Length (km) | Steel Grade | Schedule | Material Cost ($) | Labor Cost ($) | Misc ($) | ROW ($)
Breakdown of compressor by station
Station ID | Shaft power (MW) | Original Capacity (MW) | Required Additional Capacity (hp) | Cost (2020$) | Revamp Cost (2020$) | Fuel usage (MMBTU/hr) | Electric power (kW)
C_0_0 | 6.0759 | 0 | 8147.8777 | 15624217.3369 | 0 | 58.0719 | 0
C_0_1 | 6.0235 | 0 | 8077.6082 | 15545258.9368 | 0 | 57.5711 | 0
C_0_2 | 5.9719 | 0 | 8008.4257 | 15467564.0391 | 0 | 57.078 | 0
CS1 | 5.9211 | 12.5 | 0 | 0 | 16916025.6901 | 56.5926 | 0
C_1_0 | 5.3703 | 0 | 7201.7363 | 14564695.1959 | 0 | 51.3286 | 0
C_1_1 | 4.2982 | 0 | 5763.957 | 12969554.3695 | 0 | 41.0812 | 0
C_1_2 | 2.8312 | 0 | 3796.6913 | 10816163.4538 | 0 | 27.06 | 0
C_1_3 | 2.818 | 0 | 3779.013 | 10796965.5291 | 0 | 26.934 | 0
C_1_4 | 2.8049 | 0 | 3761.4779 | 10777925.7286 | 0 | 26.809 | 0
C_1_5 | 2.792 | 0 | 3744.0841 | 10759042.1113 | 0 | 26.685 | 0
C_1_6 | 2.7791 | 0 | 3726.8302 | 10740312.8901 | 0 | 26.562 | 0
CS2 | 2.7663 | 12.5 | 0 | 0 | 16916025.6901 | 26.4401 | 0
C_2_0 | 4.5285 | 0 | 6072.765 | 13310641.5843 | 0 | 43.2821 | 0
C_2_1 | 4.4928 | 0 | 6024.9501 | 13257774.3246 | 0 | 42.9413 | 0
C_2_2 | 4.4577 | 0 | 5977.8214 | 13205685.2886 | 0 | 42.6054 | 0
CS3 | 4.423 | 12.5 | 0 | 0 | 16916025.6901 | 42.2741 | 0
C_3_0 | 4.3888 | 0 | 5885.5113 | 13103715.4374 | 0 | 41.9475 | 0
C_3_1 | 4.3551 | 0 | 5840.3082 | 13053809.1971 | 0 | 41.6253 | 0
C_3_2 | 4.3219 | 0 | 5795.7284 | 13004608.449 | 0 | 41.3076 | 0

## Modified network design
Pipe segment | Pipe name | FromName | ToName | Type | Flow rate (kg/s) | DN | Schedule | Thickness (mm) | Steel grade | MAOP (MPa-g) | Length (km) | Length (mi) | Inlet pressure (Pa-g) | Outlet pressure (Pa-g) | Max velocity (m/s) | Max Mach number | Erosional velocity (m/s)
0 | PI01_0 | N01 | N01_0 | Existing | 102.387 | 650 | S Std | 9.525 | X60 | 4.7198 | 13.3333 | 8.2849 | 4719848.2732 | 4153318.6236 | 19.6713 | 0.032768 | 30.392
0 | PI01_1_pre_C_0_0 | N01_0 | N_pre_C_0_0 | Existing | 102.387 | 650 | S Std | 9.525 | X60 | 4.7198 | 4.1667 | 2.589 | 4153318.6236 | 3960095.8087 | 20.608 | 0.034373 | 31.1072
0 | PI01_1_remaining | N_post_C_0_0 | N01_1 | Existing | 102.1258 | 650 | S Std | 9.525 | X60 | 4.7198 | 9.1667 | 5.6959 | 4719848.2732 | 4340123.8 | 18.7955 | 0.031272 | 29.7458
0 | PI01_pre_C_0_1 | N01_1 | N_pre_C_0_1 | Existing | 102.1258 | 650 | S Std | 9.525 | X60 | 4.7198 | 8.3333 | 5.1781 | 4340123.8 | 3964249.0235 | 20.5344 | 0.034249 | 31.0913
0 | PI01_remaining | N_post_C_0_1 | N02 | Existing | 101.8669 | 650 | S Std | 9.525 | X60 | 4.7198 | 5 | 3.1069 | 4719848.2732 | 4517629.5176 | 18.0273 | 0.02996 | 29.1685
0 | PI02_0_pre_C_0_2 | N02 | N_pre_C_0_2 | Existing | 101.8669 | 650 | S Std | 9.525 | X60 | 4.7198 | 12.5 | 7.7671 | 4517629.5176 | 3968352.1199 | 20.4617 | 0.034127 | 31.0756
0 | PI02_0_remaining | N_post_C_0_2 | N02_0 | Existing | 101.6101 | 650 | S Std | 9.525 | X60 | 4.7198 | 2.5 | 1.5534 | 4719848.2732 | 4620320.3767 | 17.5908 | 0.029216 | 28.8496
0 | PI02 | N02_0 | N03 | Existing | 101.6101 | 650 | S Std | 9.525 | X60 | 4.7198 | 15 | 9.3206 | 4620320.3767 | 3972405.12 | 20.3898 | 0.034006 | 31.0602
1 | PI03_0 | N03_C | N03_C_0 | Existing | 101.3556 | 650 | S Std | 9.525 | X60 | 4.7198 | 15.75 | 9.7866 | 4719848.2732 | 4056742.5426 | 19.9258 | 0.033213 | 30.7433
1 | PI03_pre_C_1_0 | N03_C_0 | N_pre_C_1_0 | Existing | 101.3556 | 650 | S Std | 9.525 | X60 | 4.7198 | 0.5 | 0.31069 | 4056742.5426 | 4033949.605 | 20.0357 | 0.033402 | 30.8279
1 | PI03_remaining | N_post_C_1_0 | N04 | Existing | 101.1247 | 650 | S Std | 9.525 | X60 | 4.7198 | 15.25 | 9.4759 | 4719848.2732 | 4082487.9236 | 19.758 | 0.032928 | 30.6484
1 | PI04_0_pre_C_1_1 | N04 | N_pre_C_1_1 | Existing | 83.4664 | 650 | S Std | 9.525 | X60 | 4.7198 | 1 | 0.62137 | 4082487.9236 | 4051491.1564 | 16.4297 | 0.027387 | 30.7627
1 | PI04_0_remaining | N_post_C_1_1 | N04_0 | Existing | 83.2816 | 650 | S Std | 9.525 | X60 | 4.7198 | 15.1667 | 9.4241 | 4719848.2732 | 4296588.012 | 15.4792 | 0.025761 | 29.8927
1 | PI04_1_pre_C_1_2 | N04_0 | N_pre_C_1_2 | Existing | 83.2816 | 650 | S Std | 9.525 | X60 | 4.7198 | 1.0833 | 0.67315 | 4296588.012 | 4264784.9829 | 15.5919 | 0.025954 | 30.0014
1 | PI04_1_remaining | N_post_C_1_2 | N04_1 | Existing | 83.1599 | 650 | S Std | 9.525 | X60 | 4.7198 | 15.0833 | 9.3723 | 4719848.2732 | 4300284.7187 | 15.4435 | 0.025701 | 29.8801
1 | PI04_pre_C_1_3 | N04_1 | N_pre_C_1_3 | Existing | 83.1599 | 650 | S Std | 9.525 | X60 | 4.7198 | 1.1667 | 0.72493 | 4300284.7187 | 4266152.8997 | 15.5643 | 0.025908 | 29.9967
1 | PI04_remaining | N_post_C_1_3 | N05 | Existing | 83.0387 | 650 | S Std | 9.525 | X60 | 4.7198 | 15 | 9.3206 | 4719848.2732 | 4303956.8206 | 15.4082 | 0.025642 | 29.8677
1 | PI05_0_pre_C_1_4 | N05 | N_pre_C_1_4 | Existing | 83.0387 | 650 | S Std | 9.525 | X60 | 4.7198 | 1.25 | 0.77671 | 4303956.8206 | 4267512.0919 | 15.5368 | 0.025862 | 29.992
1 | PI05_0_remaining | N_post_C_1_4 | N05_0 | Existing | 82.9181 | 650 | S Std | 9.525 | X60 | 4.7198 | 15.4167 | 9.5795 | 4719848.2732 | 4293116.3939 | 15.4238 | 0.025669 | 29.9045
1 | PI05_1_pre_C_1_5 | N05_0 | N_pre_C_1_5 | Existing | 82.9181 | 650 | S Std | 9.525 | X60 | 4.7198 | 0.83333 | 0.51781 | 4293116.3939 | 4268862.6524 | 15.5094 | 0.025816 | 29.9874
1 | PI05_1_remaining | N_post_C_1_5 | N05_1 | Existing | 82.7981 | 650 | S Std | 9.525 | X60 | 4.7198 | 15.8333 | 9.8384 | 4719848.2732 | 4282310.2853 | 15.4394 | 0.025697 | 29.9413
1 | PI05_pre_C_1_6 | N05_1 | N_pre_C_1_6 | Existing | 82.7981 | 650 | S Std | 9.525 | X60 | 4.7198 | 0.41667 | 0.2589 | 4282310.2853 | 4270204.6604 | 15.4822 | 0.02577 | 29.9828
1 | PI05_remaining | N_post_C_1_6 | N06 | Existing | 82.6786 | 650 | S Std | 9.525 | X60 | 4.7198 | 16.25 | 10.0973 | 4719848.2732 | 4271538.1998 | 15.4551 | 0.025725 | 29.9782
2 | PI06_0 | N06_C | N06_C_0 | Existing | 82.5597 | 650 | S Std | 9.525 | X60 | 4.7198 | 16.6667 | 10.3562 | 4719848.2732 | 4260799.8457 | 15.4709 | 0.025753 | 30.0151
2 | PI06_1_pre_C_2_0 | N06_C_0 | N_pre_C_2_0 | Existing | 82.5597 | 650 | S Std | 9.525 | X60 | 4.7198 | 8.3333 | 5.1781 | 4260799.8457 | 4012102.6565 | 16.407 | 0.027356 | 30.9098
2 | PI06_1_remaining | N_post_C_2_0 | N06_C_1 | Existing | 82.365 | 650 | S Std | 9.525 | X60 | 4.7198 | 8.3333 | 5.1781 | 4719848.2732 | 4497112.976 | 14.6411 | 0.024336 | 29.2335
2 | PI06 | N06_C_1 | N_pre_C_2_1 | Existing | 82.365 | 650 | S Std | 9.525 | X60 | 4.7198 | 16.6667 | 10.3562 | 4497112.976 | 4015643.837 | 16.3542 | 0.027267 | 30.8965
2 | PI07_0_remaining | N07 | N07_0 | Existing | 82.1718 | 650 | S Std | 9.525 | X60 | 4.7198 | 16.6667 | 10.3562 | 4719848.2732 | 4265228.1728 | 15.3826 | 0.025605 | 29.9999
2 | PI07_1_pre_C_2_2 | N07_0 | N_pre_C_2_2 | Existing | 82.1718 | 650 | S Std | 9.525 | X60 | 4.7198 | 8.3333 | 5.1781 | 4265228.1728 | 4019144.6298 | 16.3019 | 0.02718 | 30.8833
2 | PI07_1_remaining | N_post_C_2_2 | N07_1 | Existing | 81.9802 | 650 | S Std | 9.525 | X60 | 4.7198 | 8.3333 | 5.1781 | 4719848.2732 | 4499192.6589 | 14.5661 | 0.024211 | 29.2269
2 | PI07 | N07_1 | N08 | Existing | 81.9802 | 650 | S Std | 9.525 | X60 | 4.7198 | 16.6667 | 10.3562 | 4499192.6589 | 4022608.4316 | 16.2503 | 0.027093 | 30.8703
3 | PI08_0 | N08_C | N08_C_0 | Existing | 81.79 | 650 | S Std | 9.525 | X60 | 4.7198 | 16.6667 | 10.3562 | 4719848.2732 | 4269563.3378 | 15.2959 | 0.02546 | 29.985
3 | PI08_1_pre_C_3_0 | N08_C_0 | N_pre_C_3_0 | Existing | 81.79 | 650 | S Std | 9.525 | X60 | 4.7198 | 8.3333 | 5.1781 | 4269563.3378 | 4026033.7153 | 16.1991 | 0.027007 | 30.8575
3 | PI08_1_remaining | N_post_C_3_0 | N08_C_1 | Existing | 81.6014 | 650 | S Std | 9.525 | X60 | 4.7198 | 8.3333 | 5.1781 | 4719848.2732 | 4501229.9735 | 14.4924 | 0.024088 | 29.2204
3 | PI08 | N08_C_1 | N_pre_C_3_1 | Existing | 81.6014 | 650 | S Std | 9.525 | X60 | 4.7198 | 16.6667 | 10.3562 | 4501229.9735 | 4029422.7962 | 16.1485 | 0.026922 | 30.8449
3 | PI09_0_remaining | N09 | N09_0 | Existing | 81.4141 | 650 | S Std | 9.525 | X60 | 4.7198 | 16.6667 | 10.3562 | 4719848.2732 | 4273808.4295 | 15.2109 | 0.025318 | 29.9704
3 | PI09_1_pre_C_3_2 | N09_0 | N_pre_C_3_2 | Existing | 81.4141 | 650 | S Std | 9.525 | X60 | 4.7198 | 8.3333 | 5.1781 | 4273808.4295 | 4032775.1417 | 16.0983 | 0.026838 | 30.8323
3 | PI09_1_remaining | N_post_C_3_2 | N09_1 | Existing | 81.2283 | 650 | S Std | 9.525 | X60 | 4.7198 | 8.3333 | 5.1781 | 4719848.2732 | 4503226.282 | 14.4199 | 0.023967 | 29.2141
3 | PI09 | N09_1 | N10 | Existing | 81.2283 | 650 | S Std | 9.525 | X60 | 4.7198 | 16.6667 | 10.3562 | 4503226.282 | 4036092.0341 | 16.0487 | 0.026754 | 30.82

## Compressor design
Segment | Name | FromName | ToName | Type | Cumulative length (km) | Cumulative length (mi) | Pressure Ratio | Fuel consumption (MMBTU/hr) | Shaft power (MW) | Shaft power (hp) | Electric power (kW) | Rating (MW) | Isentropic efficiency | Driver efficiency | Cost ($) | Revamp cost ($) | Total cost ($)
0 | C_0_0 | N_pre_C_0_0 | N_post_C_0_0 | New | 17.5 | 10.874 | 1.1919 | 58.0719 | 6.0759 | 8147.8777 | 0 | 6.0759 | 0.78 | 0.357 | 15624217.3369 | 0 | 15624217.3369
0 | C_0_1 | N_pre_C_0_1 | N_post_C_0_1 | New | 35 | 21.748 | 1.1906 | 57.5711 | 6.0235 | 8077.6082 | 0 | 6.0235 | 0.78 | 0.357 | 15545258.9368 | 0 | 15545258.9368
0 | C_0_2 | N_pre_C_0_2 | N_post_C_0_2 | New | 52.5 | 32.622 | 1.1894 | 57.078 | 5.9719 | 8008.4257 | 0 | 5.9719 | 0.78 | 0.357 | 15467564.0391 | 0 | 15467564.0391
| CS1 | N03 | N03_C | Existing | 70 | 43.496 | 1.1882 | 56.5926 | 5.9211 | 7940.3172 | 0 | 12.5 | 0.78 | 0.357 | 0 | 16916025.6901 | 16916025.6901
1 | C_1_0 | N_pre_C_1_0 | N_post_C_1_0 | New | 86.25 | 53.5932 | 1.17 | 51.3286 | 5.3703 | 7201.7363 | 0 | 5.3703 | 0.78 | 0.357 | 14564695.1959 | 0 | 14564695.1959
1 | C_1_1 | N_pre_C_1_1 | N_post_C_1_1 | New | 102.5 | 63.6905 | 1.165 | 41.0812 | 4.2982 | 5763.957 | 0 | 4.2982 | 0.78 | 0.357 | 12969554.3695 | 0 | 12969554.3695
1 | C_1_2 | N_pre_C_1_2 | N_post_C_1_2 | New | 118.75 | 73.7878 | 1.1067 | 27.06 | 2.8312 | 3796.6913 | 0 | 2.8312 | 0.78 | 0.357 | 10816163.4538 | 0 | 10816163.4538
1 | C_1_3 | N_pre_C_1_3 | N_post_C_1_3 | New | 135 | 83.8851 | 1.1063 | 26.934 | 2.818 | 3779.013 | 0 | 2.818 | 0.78 | 0.357 | 10796965.5291 | 0 | 10796965.5291
1 | C_1_4 | N_pre_C_1_4 | N_post_C_1_4 | New | 151.25 | 93.9824 | 1.106 | 26.809 | 2.8049 | 3761.4779 | 0 | 2.8049 | 0.78 | 0.357 | 10777925.7286 | 0 | 10777925.7286
1 | C_1_5 | N_pre_C_1_5 | N_post_C_1_5 | New | 167.5 | 104.0796 | 1.1056 | 26.685 | 2.792 | 3744.0841 | 0 | 2.792 | 0.78 | 0.357 | 10759042.1113 | 0 | 10759042.1113
1 | C_1_6 | N_pre_C_1_6 | N_post_C_1_6 | New | 183.75 | 114.1769 | 1.1053 | 26.562 | 2.7791 | 3726.8302 | 0 | 2.7791 | 0.78 | 0.357 | 10740312.8901 | 0 | 10740312.8901
| CS2 | N06 | N06_C | Existing | 200 | 124.2742 | 1.105 | 26.4401 | 2.7663 | 3709.7145 | 0 | 12.5 | 0.78 | 0.357 | 0 | 16916025.6901 | 16916025.6901
2 | C_2_0 | N_pre_C_2_0 | N_post_C_2_0 | New | 225 | 139.8085 | 1.1764 | 43.2821 | 4.5285 | 6072.765 | 0 | 4.5285 | 0.78 | 0.357 | 13310641.5843 | 0 | 13310641.5843
2 | C_2_1 | N_pre_C_2_1 | N07 | New | 250 | 155.3427 | 1.1754 | 42.9413 | 4.4928 | 6024.9501 | 0 | 4.4928 | 0.78 | 0.357 | 13257774.3246 | 0 | 13257774.3246
2 | C_2_2 | N_pre_C_2_2 | N_post_C_2_2 | New | 275 | 170.877 | 1.1743 | 42.6054 | 4.4577 | 5977.8214 | 0 | 4.4577 | 0.78 | 0.357 | 13205685.2886 | 0 | 13205685.2886
| CS3 | N08 | N08_C | Existing | 300 | 186.4113 | 1.1733 | 42.2741 | 4.423 | 5931.3395 | 0 | 12.5 | 0.78 | 0.357 | 0 | 16916025.6901 | 16916025.6901
3 | C_3_0 | N_pre_C_3_0 | N_post_C_3_0 | New | 325 | 201.9456 | 1.1723 | 41.9475 | 4.3888 | 5885.5113 | 0 | 4.3888 | 0.78 | 0.357 | 13103715.4374 | 0 | 13103715.4374
3 | C_3_1 | N_pre_C_3_1 | N09 | New | 350 | 217.4798 | 1.1713 | 41.6253 | 4.3551 | 5840.3082 | 0 | 4.3551 | 0.78 | 0.357 | 13053809.1971 | 0 | 13053809.1971
3 | C_3_2 | N_pre_C_3_2 | N_post_C_3_2 | New | 375 | 233.0141 | 1.1704 | 41.3076 | 4.3219 | 5795.7284 | 0 | 4.3219 | 0.78 | 0.357 | 13004608.449 | 0 | 13004608.449

## Pressure profile
Node | Pressure (Pa-g)
N01 | 4719848.2732
N01_0 | 4153318.6236
N_pre_C_0_0 | 3960095.8087
N_post_C_0_0 | 4719848.2732
N01_1 | 4340123.8
N_pre_C_0_1 | 3964249.0235
N_post_C_0_1 | 4719848.2732
N02 | 4517629.5176
N_pre_C_0_2 | 3968352.1199
N_post_C_0_2 | 4719848.2732
N02_0 | 4620320.3767
N03 | 3972405.12
N03_C | 4719848.2732
N03_C_0 | 4056742.5426
N_pre_C_1_0 | 4033949.605
N_post_C_1_0 | 4719848.2732
N04 | 4082487.9236
N_pre_C_1_1 | 4051491.1564
N_post_C_1_1 | 4719848.2732
N04_0 | 4296588.012
N_pre_C_1_2 | 4264784.9829
N_post_C_1_2 | 4719848.2732
N04_1 | 4300284.7187
N_pre_C_1_3 | 4266152.8997
N_post_C_1_3 | 4719848.2732
N05 | 4303956.8206
N_pre_C_1_4 | 4267512.0919
N_post_C_1_4 | 4719848.2732
N05_0 | 4293116.3939
N_pre_C_1_5 | 4268862.6524
N_post_C_1_5 | 4719848.2732
N05_1 | 4282310.2853
N_pre_C_1_6 | 4270204.6604
N_post_C_1_6 | 4719848.2732
N06 | 4271538.1998
N06_C | 4719848.2732
N06_C_0 | 4260799.8457
N_pre_C_2_0 | 4012102.6565
N_post_C_2_0 | 4719848.2732
N06_C_1 | 4497112.976
N07 | 4719848.2732
N_pre_C_2_1 | 4015643.837
N07_0 | 4265228.1728
N_pre_C_2_2 | 4019144.6298
N_post_C_2_2 | 4719848.2732
N07_1 | 4499192.6589
N08 | 4022608.4316
N08_C | 4719848.2732
N08_C_0 | 4269563.3378
N_pre_C_3_0 | 4026033.7153
N_post_C_3_0 | 4719848.2732
N08_C_1 | 4501229.9735
N09 | 4719848.2732
N_pre_C_3_1 | 4029422.7962
N09_0 | 4273808.4295
N_pre_C_3_2 | 4032775.1417
N_post_C_3_2 | 4719848.2732
N09_1 | 4503226.282
N10 | 4036092.0341

## Demand error
Demand node name | Flow rate set point (kg/s) | Flow rate calculated (kg/s) | Higher heating value (MJ/kg) | Energy set point (MW) | Energy calculated (MW) | Error in energy (%)
N04 | 17.6583 | 17.6583 | 65.1545 | 1150.5204 | 1150.5204 | -1.8188e-11
N10 | 45.9117 | 45.9117 | 65.1545 | 2991.353 | 2991.353 | 3.0953e-14
N13 | 35.3167 | 35.3167 | 65.1545 | 2301.0408 | 2301.0408 | 4.0238e-14

## ProFAST
capacity | 527617.1846909181
long term utilization | 1
demand rampup | 0
analysis start year | 2020
operating life | 50
installation months | 36
TOPC | unit price | 0.0 | decay | 0.0 | support utilization | 0.0 | sunset years | 0
commodity | name | Natural Gas-H2 Blend | unit | MMBTU | initial price | 0.25 | escalation | 0.025
annual operating incentive | value | 0.0 | decay | 0.0 | sunset years | 0 | taxable | True
incidental revenue | value | 0.0 | escalation | 0.0
credit card fees | 0.0
sales tax | 0.0
road tax | value | 0.0 | escalation | 0.0
labor | value | 0.0 | rate | 0.0 | escalation | 0.0
maintenance | value | 0.0 | escalation | 0.0
rent | value | 0.0 | escalation | 0.0
license and permit | value | 0.0 | escalation | 0.0
non depr assets | 0.0
end of proj sale non depr assets | 0.0
installation cost | value | 0.0 | depr type | Straight line | depr period | 3 | depreciable | True
one time cap inct | value | 0.0 | depr type | MACRS | depr period | 3 | depreciable | True
property tax and insurance | 0.009
admin expense | 0.005
tax loss carry forward years | 0
capital gains tax rate | 0.15
tax losses monetized | True
sell undepreciated cap | True
loan period if used | 0
debt equity ratio of initial financing | 0.62
debt interest rate | 0.07
debt type | Revolving debt
total income tax rate | 0.2574
cash onhand | 3
general inflation rate | 0.025
leverage after tax nominal discount rate | 0.13
fraction of year operated | [0. 0. 0. 0. 1. 1. 1. 1. 1. 1. 1. 1. 1. 1. 1. 1. 1. 1. 1. 1. 1. 1. 1. 1. 1. 1. 1. 1. 1. 1. 1. 1. 1. 1. 1. 1. 1. 1. 1. 1. 1. 1. 1. 1. 1. 1. 1. 1. 1. 1. 1. 1. 1. 1.]
New pipe CapEx | cost | 0 | depr_type | Straight line | depr_period | 50 | refurb | [0]
New compression capacity CapEx | cost | 206997933.87205377 | depr_type | Straight line | depr_period | 50 | refurb | [0]
Refurbished compressor capacity CapEx | cost | 50748077.07023712 | depr_type | Straight line | depr_period | 50 | refurb | [0]
Supply compressor CapEx | cost | 0 | depr_type | Straight line | depr_period | 50 | refurb | [0]
Meter & regulator station modification CapEx | cost | 10486757.29473448 | depr_type | Straight line | depr_period | 50 | refurb | [0]
Valve replacement CapEx | cost | 24862120.0 | depr_type | Straight line | depr_period | 50 | refurb | [0]
Original network residual value | cost | 0.0 | depr_type | Straight line | depr_period | 50 | refurb | [0]
Meter set assembly | cost | 0 | depr_type | Straight line | depr_period | 50 | refurb | [0]
Gas pressure regulation and metering station | cost | 0 | depr_type | Straight line | depr_period | 50 | refurb | [0]
Compressor fuel | cost | {'2048': np.float64(27.046985282253413), '2049': np.float64(27.723159914309747), '2050': np.float64(28.416238912167486), '2051': np.float64(29.126644884971675), '2052': np.float64(29.85481100709596), '2053': np.float64(30.60118128227336), '2054': np.float64(31.366210814330188), '2055': np.float64(32.150366084688436), '2056': np.float64(32.954125236805645), '2057': np.float64(33.77797836772578), '2058': np.float64(34.62242782691893), '2059': np.float64(35.48798852259189), '2060': np.float64(36.37518823565669), '2061': np.float64(37.284567941548104), '2062': np.float64(38.2166821400868), '2063': np.float64(39.17209919358897), '2064': np.float64(40.151401673428694), '2065': np.float64(41.155186715264406), '2066': np.float64(42.18406638314601), '2067': np.float64(43.238668042724655), '2068': np.float64(44.319634743792776), '2069': np.float64(45.42762561238759), '2070': np.float64(46.56331625269728), '2071': np.float64(47.7273991590147), '2072': np.float64(48.92058413799006), '2073': np.float64(50.14359874143982), '2074': np.float64(51.3971887099758), '2075': np.float64(52.68211842772519), '2076': np.float64(53.99917138841832), '2077': np.float64(55.34915067312877), '2078': np.float64(56.732879439956996), '2079': np.float64(58.1512014259559), '2080': np.float64(59.604981461604794), '2081': np.float64(61.095105998144916), '2082': np.float64(62.62248364809852), '2020': np.float64(13.54723404173073), '2021': np.float64(13.885914892773997), '2022': np.float64(14.233062765093345), '2023': np.float64(14.588889334220678), '2024': np.float64(14.953611567576193), '2025': np.float64(15.327451856765595), '2026': np.float64(15.710638153184735), '2027': np.float64(16.103404107014356), '2028': np.float64(16.50598920968971), '2029': np.float64(16.918638939931952), '2030': np.float64(17.341604913430245), '2031': np.float64(17.775145036266004), '2032': np.float64(18.219523662172655), '2033': np.float64(18.675011753726963), '2034': np.float64(19.14188704757014), '2035': np.float64(19.62043422375939), '2036': np.float64(20.110945079353375), '2037': np.float64(20.613718706337206), '2038': np.float64(21.129061673995636), '2039': np.float64(21.65728821584552), '2040': np.float64(22.19872042124166), '2041': np.float64(22.7536884317727), '2042': np.float64(23.322530642567017), '2043': np.float64(23.90559390863119), '2044': np.float64(24.503233756346965), '2045': np.float64(25.11581460025564), '2046': np.float64(25.743709965262028), '2047': np.float64(26.387302714393577)} | usage | 0.03539824745318141 | escalation | 0.025
Compressor fuel (electric) | cost | 0.07 | usage | 0.0 | escalation | 0.025
Supply commpressor fuel (electric) | cost | 0.07 | usage | 0.0 | escalation | 0.025
Supply commpressor fuel | cost | {'2048': np.float64(27.046985282253413), '2049': np.float64(27.723159914309747), '2050': np.float64(28.416238912167486), '2051': np.float64(29.126644884971675), '2052': np.float64(29.85481100709596), '2053': np.float64(30.60118128227336), '2054': np.float64(31.366210814330188), '2055': np.float64(32.150366084688436), '2056': np.float64(32.954125236805645), '2057': np.float64(33.77797836772578), '2058': np.float64(34.62242782691893), '2059': np.float64(35.48798852259189), '2060': np.float64(36.37518823565669), '2061': np.float64(37.284567941548104), '2062': np.float64(38.2166821400868), '2063': np.float64(39.17209919358897), '2064': np.float64(40.151401673428694), '2065': np.float64(41.155186715264406), '2066': np.float64(42.18406638314601), '2067': np.float64(43.238668042724655), '2068': np.float64(44.319634743792776), '2069': np.float64(45.42762561238759), '2070': np.float64(46.56331625269728), '2071': np.float64(47.7273991590147), '2072': np.float64(48.92058413799006), '2073': np.float64(50.14359874143982), '2074': np.float64(51.3971887099758), '2075': np.float64(52.68211842772519), '2076': np.float64(53.99917138841832), '2077': np.float64(55.34915067312877), '2078': np.float64(56.732879439956996), '2079': np.float64(58.1512014259559), '2080': np.float64(59.604981461604794), '2081': np.float64(61.095105998144916), '2082': np.float64(62.62248364809852), '2020': np.float64(13.54723404173073), '2021': np.float64(13.885914892773997), '2022': np.float64(14.233062765093345), '2023': np.float64(14.588889334220678), '2024': np.float64(14.953611567576193), '2025': np.float64(15.327451856765595), '2026': np.float64(15.710638153184735), '2027': np.float64(16.103404107014356), '2028': np.float64(16.50598920968971), '2029': np.float64(16.918638939931952), '2030': np.float64(17.341604913430245), '2031': np.float64(17.775145036266004), '2032': np.float64(18.219523662172655), '2033': np.float64(18.675011753726963), '2034': np.float64(19.14188704757014), '2035': np.float64(19.62043422375939), '2036': np.float64(20.110945079353375), '2037': np.float64(20.613718706337206), '2038': np.float64(21.129061673995636), '2039': np.float64(21.65728821584552), '2040': np.float64(22.19872042124166), '2041': np.float64(22.7536884317727), '2042': np.float64(23.322530642567017), '2043': np.float64(23.90559390863119), '2044': np.float64(24.503233756346965), '2045': np.float64(25.11581460025564), '2046': np.float64(25.743709965262028), '2047': np.float64(26.387302714393577)} | usage | 0.0 | escalation | 0.025
In-line inspection | cost | 3277333.333333334 | escalation | 0.025