## Disclaimer
---------DISCLAIMER--------- AS NOTED IN THE LICENSE, ALLIANCE FOR ENERGY INNOVATION, LLC: (i) DISCLAIMS ANY WARRANTIES, EXPRESS OR IMPLIED, INCLUDING BUT NOT LIMITED TO ANY IMPLIED WARRANTIES OF MERCHANTABILITY, FITNESS FOR A PARTICULAR PURPOSE, TITLE OR NON-INFRINGEMENT, AND (ii) DOES NOT ASSUME ANY LEGAL LIABILITY OR RESPONSIBILITY FOR THE ACCURACY, COMPLETENESS, OR USEFULNESS OF SOFTWARE OR ITS OUTPUTS. ANY RELIANCE BY THE USER ON THE SOFTWARE IS DONE AT THE USER’S OWN RISK. BlendPATH was developed to provide the user with economic analytical capabilities to evaluate potential natural gas transmission pipeline modifications for accommodating hydrogen blending or pure hydrogen streams and to assess the potential associated economic impacts. This model is intended for use during the early stages of pipeline repurposing concept evaluation, which is defined here as the initial project phase when the developer has already gathered the relevant pipeline material design and operation data but has not yet conducted the detailed pipeline materials testing, as specified in ASME B31.12, or performed the in-line inspections that qualify a given pipeline section for hydrogen or hydrogen blending service. Despite BlendPATH using ASME B31.12 to assess existing natural gas transmission pipelines and establish potential pipeline modifications for a natural gas transmission pipeline network to meet ASME B31.12 design requirements, BlendPATH does not qualify the examined pipeline network or modifications thereof for pure hydrogen or hydrogen blending. Pipeline owners and operators must conduct additional evaluations as specified in ASME B31.12 and other relevant code and regulations, independent of BlendPATH application, to qualify actual natural gas transmission pipelines for operation with hydrogen. Failure to do so may result in pipeline fatigue and/or rupture. It is the sole responsibility of the pipeline owner and operator to ensure that their pipeline qualifies for the ASME B31.12 design option that they choose, and any other relevant code and regulations, and that any defects present in the pipeline are acceptable at the operating pressure chosen. ----------------------------

## Inputs
Name | Value
Network name | examples/wangetal2018
Save directory | out
Design option - original | nfc
Location class | 1
Joint factor | 1
T de-rating factor | 1
Compression ratio | [1.2, 1.4, 1.6, 1.8, 2.0]
Blending ratio | 0.5
Natural gas cost ($/MMBTU) | 7.39
H2 cost ($/kg) | 4.4076
Electricity cost ($/kWh) | 0.07
Final outlet pressure (MPa-g) | 3.325
Region | GP
Modification method | ac
Modification design option | b
Equation of state | rk
Inline inspection inspection interval | 3
Original pipeline depreciated cost | 0
Are added compressors electric? | FALSE
Are existing compressors converted to electric? | FALSE
New gas compressor isentropic efficiency | 0.78
New electric compressor isentropic efficiency | 0.88
New gas compressor driver efficiency | 0.357
New electric compressor driver efficiency
Pipe price markup | 1
Compressor price markup | 1
Financial overrides | {}
Filename suffix
Thermodynamic curvefits enabled | TRUE
Composition tracking enabled | FALSE
Scenario type | transmission
Polymer cost type | socal
Max velocity allowed in distribution networks | 20

## Results
Parameter | Value | Units
LCOT: Levelized cost of transport | 0.70645 | $/MMBTU
LCOT: New pipe CapEx | 0 | $/MMBTU
LCOT: New compression capacity CapEx | 0.10307 | $/MMBTU
LCOT: Refurbished compressor capacity CapEx | 0.032867 | $/MMBTU
LCOT: Supply compressor CapEx | 0 | $/MMBTU
LCOT: Meter & regulator station modification CapEx | 0.0067918 | $/MMBTU
LCOT: Valve replacement CapEx | 0.016102 | $/MMBTU
LCOT: Original network residual value | 0 | $/MMBTU
LCOT: In-line inspection | 0.017018 | $/MMBTU
LCOT: Compressor fuel | 0.47566 | $/MMBTU
LCOT: Compressor fuel (electric) | 0 | $/MMBTU
LCOT: Supply commpressor fuel (electric) | 0 | $/MMBTU
LCOT: Supply commpressor fuel | 0 | $/MMBTU
LCOT: Meter set assembly | 0 | $/MMBTU
LCOT: Gas pressure regulation and metering station | 0 | $/MMBTU
LCOT: Fixed O&M | 0.0071852 | $/MMBTU
LCOT: Taxes | 0.044382 | $/MMBTU
LCOT: Financial | 0.0033753 | $/MMBTU
Hydrogen injection price | 4.4076 | $/kg
Natural gas price | 7.39 | $/MMBTU
Blended gas price | 13.5472 | $/MMBTU
Pipeline capacity (daily) | 527617.1847 | MMBTU/day
Pipeline capacity (hour) | 21984.0494 | MMBTU/hr
Added pipeline | 0 | km
Added pipeline | 0 | mi
Added compressor stations | 10
Added compressor capacity | 83908.292 | hp
Compressor fuel usage | 18525.1173 | MMBTU/day
Compressor fuel usage | 771.8799 | MMBTU/hr
Compressor fuel usage (electric) | 0 | kW
New pipe | 0 | $
New compressor stations | 159148723.5183 | $
Compressor station refurbishment | 50748077.0702 | $
Meter station modification | 10486757.2947 | $
Valve modifications | 24862120 | $
Meter set assembly | 0 | $
Gas pressure regulating metering station | 0 | $
Hydrogen energy ratio | 24.2409 | %
Emissions intensity (total) | 49.9011 | kgCO2e/MMBTU
Total emissions (annual) | 9.61 | MMTCO2e/yr
Breakdown of original pipe by diameter, schedule and grade
Pipe Nominal Diameter | Length (km) | Grade | Schedule | Polymer
650 | 400 | X60 | S Std
Breakdown of new pipe by diameter, schedule and grade
Pipe Nominal Diameter | Length (km) | Steel Grade | Schedule | Material Cost ($) | Labor Cost ($) | Misc ($) | ROW ($)
Breakdown of compressor by station
Station ID | Shaft power (MW) | Original Capacity (MW) | Required Additional Capacity (hp) | Cost (2020$) | Revamp Cost (2020$) | Fuel usage (MMBTU/hr) | Electric power (kW)
C_0_0 | 8.0856 | 0 | 10842.9304 | 18684989.6627 | 0 | 77.2803 | 0
C_0_1 | 7.9885 | 0 | 10712.8021 | 18535748.5324 | 0 | 76.3528 | 0
CS1 | 7.8936 | 12.5 | 0 | 0 | 16916025.6901 | 75.4449 | 0
C_1_0 | 8.9962 | 0 | 12064.0615 | 20092665.5798 | 0 | 85.9836 | 0
C_1_1 | 5.0893 | 0 | 6824.8792 | 14144849.9086 | 0 | 48.6426 | 0
C_1_2 | 4.5101 | 0 | 6048.0853 | 13283351.6314 | 0 | 43.1062 | 0
C_1_3 | 4.4749 | 0 | 6000.974 | 13231272.2672 | 0 | 42.7704 | 0
CS2 | 4.4403 | 12.5 | 0 | 0 | 16916025.6901 | 42.4398 | 0
C_2_0 | 5.9833 | 0 | 8023.7647 | 15484786.7892 | 0 | 57.1874 | 0
C_2_1 | 5.9185 | 0 | 7936.797 | 15387165.7534 | 0 | 56.5675 | 0
CS3 | 5.8549 | 12.5 | 0 | 0 | 16916025.6901 | 55.9599 | 0
C_3_0 | 5.7926 | 0 | 7767.9754 | 15197852.27 | 0 | 55.3643 | 0
C_3_1 | 5.7315 | 0 | 7686.0224 | 15106041.1236 | 0 | 54.7802 | 0

## Modified network design
Pipe segment | Pipe name | FromName | ToName | Type | Flow rate (kg/s) | DN | Schedule | Thickness (mm) | Steel grade | MAOP (MPa-g) | Length (km) | Length (mi) | Inlet pressure (Pa-g) | Outlet pressure (Pa-g) | Max velocity (m/s) | Max Mach number | Erosional velocity (m/s)
0 | PI01_0 | N01 | N01_0 | Existing | 102.3586 | 650 | S Std | 9.525 | X60 | 4.8658 | 13.3333 | 8.2849 | 4865822.962 | 4318363.8534 | 18.9311 | 0.031501 | 29.8189
0 | PI01_1_pre_C_0_0 | N01_0 | N_pre_C_0_0 | Existing | 102.3586 | 650 | S Std | 9.525 | X60 | 4.8658 | 10 | 6.2137 | 4318363.8534 | 3858388.136 | 21.1319 | 0.035271 | 31.5046
0 | PI01_1_remaining | N_post_C_0_0 | N01_1 | Existing | 102.011 | 650 | S Std | 9.525 | X60 | 4.8658 | 3.3333 | 2.0712 | 4865822.962 | 4735652.0572 | 17.2394 | 0.028613 | 28.5038
0 | PI01 | N01_1 | N02 | Existing | 102.011 | 650 | S Std | 9.525 | X60 | 4.8658 | 13.3333 | 8.2849 | 4735652.0572 | 4175545.3215 | 19.4971 | 0.032473 | 30.3129
0 | PI02_0_pre_C_0_1 | N02 | N_pre_C_0_1 | Existing | 102.011 | 650 | S Std | 9.525 | X60 | 4.8658 | 6.6667 | 4.1425 | 4175545.3215 | 3865932.2689 | 21.0201 | 0.035083 | 31.4746
0 | PI02_0_remaining | N_post_C_0_1 | N02_0 | Existing | 101.6676 | 650 | S Std | 9.525 | X60 | 4.8658 | 8.3333 | 5.1781 | 4865822.962 | 4535819.6862 | 17.9214 | 0.029781 | 29.1112
0 | PI02 | N02_0 | N03 | Existing | 101.6676 | 650 | S Std | 9.525 | X60 | 4.8658 | 15 | 9.3206 | 4535819.6862 | 3873357.8226 | 20.9102 | 0.034898 | 31.4451
1 | PI03_0 | N03_C | N03_C_0 | Existing | 101.3282 | 650 | S Std | 9.525 | X60 | 4.8658 | 15.75 | 9.7866 | 4865822.962 | 4225517.6428 | 19.1428 | 0.031873 | 30.1372
1 | PI03_pre_C_1_0 | N03_C_0 | N_pre_C_1_0 | Existing | 101.3282 | 650 | S Std | 9.525 | X60 | 4.8658 | 10.25 | 6.3691 | 4225517.6428 | 3752046.0766 | 21.4973 | 0.035908 | 31.9369
1 | PI03_remaining | N_post_C_1_0 | N04 | Existing | 100.9415 | 650 | S Std | 9.525 | X60 | 4.8658 | 5.5 | 3.4175 | 4865822.962 | 4653664.2628 | 17.3526 | 0.028815 | 28.7484
1 | PI04_0 | N04 | N04_0 | Existing | 83.2831 | 650 | S Std | 9.525 | X60 | 4.8658 | 16.1667 | 10.0455 | 4653664.2628 | 4194068.255 | 15.849 | 0.026394 | 30.2474
1 | PI04_1_pre_C_1_1 | N04_0 | N_pre_C_1_1 | Existing | 83.2831 | 650 | S Std | 9.525 | X60 | 4.8658 | 4.3333 | 2.6926 | 4194068.255 | 4062261.3923 | 16.3512 | 0.027254 | 30.7229
1 | PI04_1_remaining | N_post_C_1_1 | N04_1 | Existing | 83.0643 | 650 | S Std | 9.525 | X60 | 4.8658 | 11.8333 | 7.3529 | 4865822.962 | 4550938.7824 | 14.5945 | 0.02425 | 29.0639
1 | PI04_pre_C_1_2 | N04_1 | N_pre_C_1_2 | Existing | 83.0643 | 650 | S Std | 9.525 | X60 | 4.8658 | 14.1667 | 8.8028 | 4550938.7824 | 4143356.0334 | 15.9964 | 0.026648 | 30.4277
1 | PI04_remaining | N_post_C_1_2 | N05 | Existing | 82.8704 | 650 | S Std | 9.525 | X60 | 4.8658 | 2 | 1.2427 | 4865822.962 | 4814256.6148 | 13.7809 | 0.022862 | 28.2751
1 | PI05_0 | N05 | N05_0 | Existing | 82.8704 | 650 | S Std | 9.525 | X60 | 4.8658 | 16.6667 | 10.3562 | 4814256.6148 | 4361439.7481 | 15.1789 | 0.025251 | 29.6747
1 | PI05_1_pre_C_1_3 | N05_0 | N_pre_C_1_3 | Existing | 82.8704 | 650 | S Std | 9.525 | X60 | 4.8658 | 7.3333 | 4.5567 | 4361439.7481 | 4146934.6979 | 15.9456 | 0.026563 | 30.4149
1 | PI05_1_remaining | N_post_C_1_3 | N05_1 | Existing | 82.6781 | 650 | S Std | 9.525 | X60 | 4.8658 | 9.3333 | 5.7995 | 4865822.962 | 4621509.4829 | 14.3097 | 0.023767 | 28.846
1 | PI05 | N05_1 | N06 | Existing | 82.6781 | 650 | S Std | 9.525 | X60 | 4.8658 | 16.6667 | 10.3562 | 4621509.4829 | 4150466.9386 | 15.8953 | 0.026479 | 30.4022
2 | PI06_0 | N06_C | N06_C_0 | Existing | 82.4872 | 650 | S Std | 9.525 | X60 | 4.8658 | 16.6667 | 10.3562 | 4865822.962 | 4422411.8822 | 14.905 | 0.024786 | 29.474
2 | PI06_1 | N06_C_0 | N_pre_C_2_0 | Existing | 82.4872 | 650 | S Std | 9.525 | X60 | 4.8658 | 16.6667 | 10.3562 | 4422411.8822 | 3930520.9345 | 16.7245 | 0.027901 | 31.2212
2 | PI06_remaining | N06_C_1 | N07 | Existing | 82.2299 | 650 | S Std | 9.525 | X60 | 4.8658 | 16.6667 | 10.3562 | 4865822.962 | 4425244.2447 | 14.8492 | 0.024692 | 29.4647
2 | PI07_0 | N07 | N_pre_C_2_1 | Existing | 82.2299 | 650 | S Std | 9.525 | X60 | 4.8658 | 16.6667 | 10.3562 | 4425244.2447 | 3936874.3375 | 16.6461 | 0.027769 | 31.1966
2 | PI07_1_remaining | N07_0 | N07_1 | Existing | 81.9755 | 650 | S Std | 9.525 | X60 | 4.8658 | 16.6667 | 10.3562 | 4865822.962 | 4428035.718 | 14.7941 | 0.0246 | 29.4556
2 | PI07 | N07_1 | N08 | Existing | 81.9755 | 650 | S Std | 9.525 | X60 | 4.8658 | 16.6667 | 10.3562 | 4428035.718 | 3943130.1286 | 16.5689 | 0.027639 | 31.1725
3 | PI08_0 | N08_C | N08_C_0 | Existing | 81.7238 | 650 | S Std | 9.525 | X60 | 4.8658 | 16.6667 | 10.3562 | 4865822.962 | 4430787.2558 | 14.7397 | 0.02451 | 29.4467
3 | PI08_1 | N08_C_0 | N_pre_C_3_0 | Existing | 81.7238 | 650 | S Std | 9.525 | X60 | 4.8658 | 16.6667 | 10.3562 | 4430787.2558 | 3949290.7256 | 16.4929 | 0.027511 | 31.1487
3 | PI08_remaining | N08_C_1 | N09 | Existing | 81.4747 | 650 | S Std | 9.525 | X60 | 4.8658 | 16.6667 | 10.3562 | 4865822.962 | 4433499.7806 | 14.686 | 0.02442 | 29.4379
3 | PI09_0 | N09 | N_pre_C_3_1 | Existing | 81.4747 | 650 | S Std | 9.525 | X60 | 4.8658 | 16.6667 | 10.3562 | 4433499.7806 | 3955358.4625 | 16.418 | 0.027385 | 31.1254
3 | PI09_1_remaining | N09_0 | N09_1 | Existing | 81.2283 | 650 | S Std | 9.525 | X60 | 4.8658 | 16.6667 | 10.3562 | 4865822.962 | 4436174.1851 | 14.633 | 0.024331 | 29.4292
3 | PI09 | N09_1 | N10 | Existing | 81.2283 | 650 | S Std | 9.525 | X60 | 4.8658 | 16.6667 | 10.3562 | 4436174.1851 | 3961335.5936 | 16.3443 | 0.027261 | 31.1025

## Compressor design
Segment | Name | FromName | ToName | Type | Cumulative length (km) | Cumulative length (mi) | Pressure Ratio | Fuel consumption (MMBTU/hr) | Shaft power (MW) | Shaft power (hp) | Electric power (kW) | Rating (MW) | Isentropic efficiency | Driver efficiency | Cost ($) | Revamp cost ($) | Total cost ($)
0 | C_0_0 | N_pre_C_0_0 | N_post_C_0_0 | New | 23.3333 | 14.4987 | 1.2611 | 77.2803 | 8.0856 | 10842.9304 | 0 | 8.0856 | 0.78 | 0.357 | 18684989.6627 | 0 | 18684989.6627
0 | C_0_1 | N_pre_C_0_1 | N_post_C_0_1 | New | 46.6667 | 28.9973 | 1.2586 | 76.3528 | 7.9885 | 10712.8021 | 0 | 7.9885 | 0.78 | 0.357 | 18535748.5324 | 0 | 18535748.5324
| CS1 | N03 | N03_C | Existing | 70 | 43.496 | 1.2562 | 75.4449 | 7.8936 | 10585.42 | 0 | 12.5 | 0.78 | 0.357 | 0 | 16916025.6901 | 16916025.6901
1 | C_1_0 | N_pre_C_1_0 | N_post_C_1_0 | New | 96 | 59.6516 | 1.2968 | 85.9836 | 8.9962 | 12064.0615 | 0 | 8.9962 | 0.78 | 0.357 | 20092665.5798 | 0 | 20092665.5798
1 | C_1_1 | N_pre_C_1_1 | N_post_C_1_1 | New | 122 | 75.8073 | 1.1978 | 48.6426 | 5.0893 | 6824.8792 | 0 | 5.0893 | 0.78 | 0.357 | 14144849.9086 | 0 | 14144849.9086
1 | C_1_2 | N_pre_C_1_2 | N_post_C_1_2 | New | 148 | 91.9629 | 1.1744 | 43.1062 | 4.5101 | 6048.0853 | 0 | 4.5101 | 0.78 | 0.357 | 13283351.6314 | 0 | 13283351.6314
1 | C_1_3 | N_pre_C_1_3 | N_post_C_1_3 | New | 174 | 108.1186 | 1.1734 | 42.7704 | 4.4749 | 6000.974 | 0 | 4.4749 | 0.78 | 0.357 | 13231272.2672 | 0 | 13231272.2672
| CS2 | N06 | N06_C | Existing | 200 | 124.2742 | 1.1724 | 42.4398 | 4.4403 | 5954.5868 | 0 | 12.5 | 0.78 | 0.357 | 0 | 16916025.6901 | 16916025.6901
2 | C_2_0 | N_pre_C_2_0 | N06_C_1 | New | 233.3333 | 144.9866 | 1.238 | 57.1874 | 5.9833 | 8023.7647 | 0 | 5.9833 | 0.78 | 0.357 | 15484786.7892 | 0 | 15484786.7892
2 | C_2_1 | N_pre_C_2_1 | N07_0 | New | 266.6667 | 165.6989 | 1.236 | 56.5675 | 5.9185 | 7936.797 | 0 | 5.9185 | 0.78 | 0.357 | 15387165.7534 | 0 | 15387165.7534
| CS3 | N08 | N08_C | Existing | 300 | 186.4113 | 1.234 | 55.9599 | 5.8549 | 7851.5507 | 0 | 12.5 | 0.78 | 0.357 | 0 | 16916025.6901 | 16916025.6901
3 | C_3_0 | N_pre_C_3_0 | N08_C_1 | New | 333.3333 | 207.1237 | 1.2321 | 55.3643 | 5.7926 | 7767.9754 | 0 | 5.7926 | 0.78 | 0.357 | 15197852.27 | 0 | 15197852.27
3 | C_3_1 | N_pre_C_3_1 | N09_0 | New | 366.6667 | 227.836 | 1.2302 | 54.7802 | 5.7315 | 7686.0224 | 0 | 5.7315 | 0.78 | 0.357 | 15106041.1236 | 0 | 15106041.1236

## Pressure profile
Node | Pressure (Pa-g)
N01 | 4865822.962
N01_0 | 4318363.8534
N_pre_C_0_0 | 3858388.136
N_post_C_0_0 | 4865822.962
N01_1 | 4735652.0572
N02 | 4175545.3215
N_pre_C_0_1 | 3865932.2689
N_post_C_0_1 | 4865822.962
N02_0 | 4535819.6862
N03 | 3873357.8226
N03_C | 4865822.962
N03_C_0 | 4225517.6428
N_pre_C_1_0 | 3752046.0766
N_post_C_1_0 | 4865822.962
N04 | 4653664.2628
N04_0 | 4194068.255
N_pre_C_1_1 | 4062261.3923
N_post_C_1_1 | 4865822.962
N04_1 | 4550938.7824
N_pre_C_1_2 | 4143356.0334
N_post_C_1_2 | 4865822.962
N05 | 4814256.6148
N05_0 | 4361439.7481
N_pre_C_1_3 | 4146934.6979
N_post_C_1_3 | 4865822.962
N05_1 | 4621509.4829
N06 | 4150466.9386
N06_C | 4865822.962
N06_C_0 | 4422411.8822
N06_C_1 | 4865822.962
N_pre_C_2_0 | 3930520.9345
N07 | 4425244.2447
N07_0 | 4865822.962
N_pre_C_2_1 | 3936874.3375
N07_1 | 4428035.718
N08 | 3943130.1286
N08_C | 4865822.962
N08_C_0 | 4430787.2558
N08_C_1 | 4865822.962
N_pre_C_3_0 | 3949290.7256
N09 | 4433499.7806
N09_0 | 4865822.962
N_pre_C_3_1 | 3955358.4625
N09_1 | 4436174.1851
N10 | 3961335.5936

## Demand error
Demand node name | Flow rate set point (kg/s) | Flow rate calculated (kg/s) | Higher heating value (MJ/kg) | Energy set point (MW) | Energy calculated (MW) | Error in energy (%)
N04 | 17.6583 | 17.6583 | 65.1545 | 1150.5204 | 1150.5204 | -7.3717e-11
N10 | 45.9117 | 45.9117 | 65.1545 | 2991.353 | 2991.353 | 6.1905e-14
N13 | 35.3167 | 35.3167 | 65.1545 | 2301.0408 | 2301.0408 | 8.0477e-14

## ProFAST
capacity | 527617.1846909181
long term utilization | 1
demand rampup | 0
analysis start year | 2020
operating life | 50
installation months | 36
TOPC | unit price | 0.0 | decay | 0.0 | support utilization | 0.0 | sunset years | 0
commodity | name | Natural Gas-H2 Blend | unit | MMBTU | initial price | 0.25 | escalation | 0.025
annual operating incentive | value | 0.0 | decay | 0.0 | sunset years | 0 | taxable | True
incidental revenue | value | 0.0 | escalation | 0.0
credit card fees | 0.0
sales tax | 0.0
road tax | value | 0.0 | escalation | 0.0
labor | value | 0.0 | rate | 0.0 | escalation | 0.0
maintenance | value | 0.0 | escalation | 0.0
rent | value | 0.0 | escalation | 0.0
license and permit | value | 0.0 | escalation | 0.0
non depr assets | 0.0
end of proj sale non depr assets | 0.0
installation cost | value | 0.0 | depr type | Straight line | depr period | 3 | depreciable | True
one time cap inct | value | 0.0 | depr type | MACRS | depr period | 3 | depreciable | True
property tax and insurance | 0.009
admin expense | 0.005
tax loss carry forward years | 0
capital gains tax rate | 0.15
tax losses monetized | True
sell undepreciated cap | True
loan period if used | 0
debt equity ratio of initial financing | 0.62
debt interest rate | 0.07
debt type | Revolving debt
total income tax rate | 0.2574
cash onhand | 3
general inflation rate | 0.025
leverage after tax nominal discount rate | 0.13
fraction of year operated | [0. 0. 0. 0. 1. 1. 1. 1. 1. 1. 1. 1. 1. 1. 1. 1. 1. 1. 1. 1. 1. 1. 1. 1. 1. 1. 1. 1. 1. 1. 1. 1. 1. 1. 1. 1. 1. 1. 1. 1. 1. 1. 1. 1. 1. 1. 1. 1. 1. 1. 1. 1. 1. 1.]
New pipe CapEx | cost | 0 | depr_type | Straight line | depr_period | 50 | refurb | [0]
New compression capacity CapEx | cost | 159148723.5183168 | depr_type | Straight line | depr_period | 50 | refurb | [0]
Refurbished compressor capacity CapEx | cost | 50748077.07023712 | depr_type | Straight line | depr_period | 50 | refurb | [0]
Supply compressor CapEx | cost | 0 | depr_type | Straight line | depr_period | 50 | refurb | [0]
Meter & regulator station modification CapEx | cost | 10486757.29473448 | depr_type | Straight line | depr_period | 50 | refurb | [0]
Valve replacement CapEx | cost | 24862120.0 | depr_type | Straight line | depr_period | 50 | refurb | [0]
Original network residual value | cost | 0.0 | depr_type | Straight line | depr_period | 50 | refurb | [0]
Meter set assembly | cost | 0 | depr_type | Straight line | depr_period | 50 | refurb | [0]
Gas pressure regulation and metering station | cost | 0 | depr_type | Straight line | depr_period | 50 | refurb | [0]
Compressor fuel | cost | {'2048': np.float64(27.046985282253413), '2049': np.float64(27.723159914309747), '2050': np.float64(28.416238912167486), '2051': np.float64(29.126644884971675), '2052': np.float64(29.85481100709596), '2053': np.float64(30.60118128227336), '2054': np.float64(31.366210814330188), '2055': np.float64(32.150366084688436), '2056': np.float64(32.954125236805645), '2057': np.float64(33.77797836772578), '2058': np.float64(34.62242782691893), '2059': np.float64(35.48798852259189), '2060': np.float64(36.37518823565669), '2061': np.float64(37.284567941548104), '2062': np.float64(38.2166821400868), '2063': np.float64(39.17209919358897), '2064': np.float64(40.151401673428694), '2065': np.float64(41.155186715264406), '2066': np.float64(42.18406638314601), '2067': np.float64(43.238668042724655), '2068': np.float64(44.319634743792776), '2069': np.float64(45.42762561238759), '2070': np.float64(46.56331625269728), '2071': np.float64(47.7273991590147), '2072': np.float64(48.92058413799006), '2073': np.float64(50.14359874143982), '2074': np.float64(51.3971887099758), '2075': np.float64(52.68211842772519), '2076': np.float64(53.99917138841832), '2077': np.float64(55.34915067312877), '2078': np.float64(56.732879439956996), '2079': np.float64(58.1512014259559), '2080': np.float64(59.604981461604794), '2081': np.float64(61.095105998144916), '2082': np.float64(62.62248364809852), '2020': np.float64(13.54723404173073), '2021': np.float64(13.885914892773997), '2022': np.float64(14.233062765093345), '2023': np.float64(14.588889334220678), '2024': np.float64(14.953611567576193), '2025': np.float64(15.327451856765595), '2026': np.float64(15.710638153184735), '2027': np.float64(16.103404107014356), '2028': np.float64(16.50598920968971), '2029': np.float64(16.918638939931952), '2030': np.float64(17.341604913430245), '2031': np.float64(17.775145036266004), '2032': np.float64(18.219523662172655), '2033': np.float64(18.675011753726963), '2034': np.float64(19.14188704757014), '2035': np.float64(19.62043422375939), '2036': np.float64(20.110945079353375), '2037': np.float64(20.613718706337206), '2038': np.float64(21.129061673995636), '2039': np.float64(21.65728821584552), '2040': np.float64(22.19872042124166), '2041': np.float64(22.7536884317727), '2042': np.float64(23.322530642567017), '2043': np.float64(23.90559390863119), '2044': np.float64(24.503233756346965), '2045': np.float64(25.11581460025564), '2046': np.float64(25.743709965262028), '2047': np.float64(26.387302714393577)} | usage | 0.03511090585402888 | escalation | 0.025
Compressor fuel (electric) | cost | 0.07 | usage | 0.0 | escalation | 0.025
Supply commpressor fuel (electric) | cost | 0.07 | usage | 0.0 | escalation | 0.025
Supply commpressor fuel | cost | {'2048': np.float64(27.046985282253413), '2049': np.float64(27.723159914309747), '2050': np.float64(28.416238912167486), '2051': np.float64(29.126644884971675), '2052': np.float64(29.85481100709596), '2053': np.float64(30.60118128227336), '2054': np.float64(31.366210814330188), '2055': np.float64(32.150366084688436), '2056': np.float64(32.954125236805645), '2057': np.float64(33.77797836772578), '2058': np.float64(34.62242782691893), '2059': np.float64(35.48798852259189), '2060': np.float64(36.37518823565669), '2061': np.float64(37.284567941548104), '2062': np.float64(38.2166821400868), '2063': np.float64(39.17209919358897), '2064': np.float64(40.151401673428694), '2065': np.float64(41.155186715264406), '2066': np.float64(42.18406638314601), '2067': np.float64(43.238668042724655), '2068': np.float64(44.319634743792776), '2069': np.float64(45.42762561238759), '2070': np.float64(46.56331625269728), '2071': np.float64(47.7273991590147), '2072': np.float64(48.92058413799006), '2073': np.float64(50.14359874143982), '2074': np.float64(51.3971887099758), '2075': np.float64(52.68211842772519), '2076': np.float64(53.99917138841832), '2077': np.float64(55.34915067312877), '2078': np.float64(56.732879439956996), '2079': np.float64(58.1512014259559), '2080': np.float64(59.604981461604794), '2081': np.float64(61.095105998144916), '2082': np.float64(62.62248364809852), '2020': np.float64(13.54723404173073), '2021': np.float64(13.885914892773997), '2022': np.float64(14.233062765093345), '2023': np.float64(14.588889334220678), '2024': np.float64(14.953611567576193), '2025': np.float64(15.327451856765595), '2026': np.float64(15.710638153184735), '2027': np.float64(16.103404107014356), '2028': np.float64(16.50598920968971), '2029': np.float64(16.918638939931952), '2030': np.float64(17.341604913430245), '2031': np.float64(17.775145036266004), '2032': np.float64(18.219523662172655), '2033': np.float64(18.675011753726963), '2034': np.float64(19.14188704757014), '2035': np.float64(19.62043422375939), '2036': np.float64(20.110945079353375), '2037': np.float64(20.613718706337206), '2038': np.float64(21.129061673995636), '2039': np.float64(21.65728821584552), '2040': np.float64(22.19872042124166), '2041': np.float64(22.7536884317727), '2042': np.float64(23.322530642567017), '2043': np.float64(23.90559390863119), '2044': np.float64(24.503233756346965), '2045': np.float64(25.11581460025564), '2046': np.float64(25.743709965262028), '2047': np.float64(26.387302714393577)} | usage | 0.0 | escalation | 0.025
In-line inspection | cost | 3277333.3333333354 | escalation | 0.025